[image: image1.png]AUTOMATIC
SISYSTEMS

[[EIR GROUP






ENGINEERING SPECIFICATIONS
SmartLane® 910 Security Entrance Lane
SECTION 11 14 00– Pedestrian Access Control Equipment (Gates/Turnstiles)

PART I – GENERAL
1.01 SECTION INCLUDES

A. This section covers the furnishing and installation of a Security Entrance Lane for pedestrian access control.
1.02 RELATED SECTIONS
** NOTE TO SPECIFIER ** Add required sections to this project

1.03 REFERENCES
B. The pedestrian security entrance lane shall be compliant with EC standards.

1.04 SYSTEM REQUIREMENTS
C. The pedestrian security entrance lane shall control and be able to restrict pedestrian traffic between public and secure areas

D. Shall feature retractable doors to securely block the pedestrian’s path and prevent access in restricted areas without authorisation
E. Shall be designed to automatically open the retractable doors by intrinsic mechanical energy in case of emergency or power failure, without any back-up battery or equivalent
F. Shall be bi-directional, allowing traffic in both directions. Each direction shall be independently configurable in one of three states:

1. Free: all persons are authorised to pass under all conditions

2. Controlled: each person must present a valid means of authentication to the reader before being authorised to pass

3. Locked: no persons are authorised to pass, and authentication means are ignored

G. Shall be designed to operate in “Normally Open” or “Normally Closed” operation mode

1. In the “Normally Closed” mode, the security entrance lane provides a closed passageway and will only open on acceptance of an authorised signal

2. In the “Normally Open” mode, the security entrance lane provides a passageway that is always open in the rest position and will only close at unauthorised entry or tailgating attempts

H. Shall use the building access control system to grant or deny access to the facility and operate with a variety of user authentication devices
I. Design of the unit shall be spacious enough to accommodate two (2) readers (one for each direction) and able to integrate the reader into its housing or to accommodate a top-mounted reader

J. Design of the unit shall feature physical and electronic security to detect and deter unauthorised use
K. Shall be designed to guarantee user safety and ease of passage
L. Design of the security entrance lane shall provide visual and audible notifications for intuitive process and high throughput
M. Shall provide equal access to people with reduced mobility

N. Can be implemented in single lane or multiple adjacent lanes and combine narrow and wide lanes in the same array
1.05 SUBMITTALS

O. Submit product data: equipment description, dimensions, electrical wiring diagrams for installation, and manufacturer's technical manuals on each product to be used, including:

1. Preparation instructions and recommendations.

2. Storage and handling requirements and recommendations.

3. Installation methods.
4. Operation and maintenance manuals.

P. Provide shop drawings and indicate component connections and location, anchorage methods and location, and installation details.

1.06 DELIVERY, STORAGE AND HANDLING

Q. Deliver equipment to job site in manufacturer’s packaging, undamaged and complete with installation instructions.

R. Store off of the ground, under cover, protected from weather, construction activities and debris.

1.07 PROJECT/SITE CONDITIONS

S. Install security entrance lane on a level finished floor.
1.08 QUALITY ASSURANCE

T. All components and sub-assemblies shall be manufactured in the European Union

U. Manufacturer Qualifications: 

1. Manufacturer shall be a company specialising in designing and manufacturing security entrance lanes with a proven minimum experience of fifteen (15) years

2. Manufacturer with well-proven experience in public transport is recommended

3. Manufacturer shall have a Quality Management System compliant with ISO 9001:2000.

V. Source Limitations: obtain Security Entrance Lanes through one source from Automatic Systems.

1.09 WARRANTY

W. Automatic Systems warranties its products against defects in material and workmanship for a period of two (2) years from the date of invoicing. This warranty excludes glass breakage, normal wear on finishes or damage that occurs due to abuse or misuse. Obtain full warranty terms from Automatic Systems.
PART II – PRODUCTS
2.01 MANUFACTURERS
X. Manufacturers: subject to compliance with requirements, provide products by one of the following:

1. AUTOMATIC SYSTEMS, 5 Avenue Mercator, 1300 Wavre, BELGIUM


Phone : +32-(0)10 230 211   Fax : +32-(0)10 230 202


Homepage : www.automatic-systems.com   E-mail : asmail@automatic-systems.com
Y. Products:

1. SmartLane® Security Entrance Lane, Model SmartLane 910
2.02 CONSTRUCTION
Z. Casing

1. To be manufactured from brushed two (2) mm thick stainless steel type AISI 304

AA. Side panels

1. Side panels shall be made of brushed two (2) mm thick stainless steel type AISI 304 and locked with security locks
AB. Top Cover
** NOTE TO SPECIFIER ** Black laminate is the standard finish for the top cover. For an additional cost, other finishes are available as options listed in brackets to perfectly suit all architectural surroundings.
Delete the following subparagraphs in brackets if no optional finish is required, or retain as necessary.
1. To be manufactured from black laminate
2. [Brushed stainless steel type AISI 304]
3. [Wood: laminated beech]
AC. Retractable doors

1. To be manufactured from monolithic clear twelve (12) mm thick tempered glass

AD. Enclosure

1. Design of the unit’s enclosure shall ensure an IP 40 degree of protection

2.03 DIMENSIONS
AE. Lane width:
** NOTE TO SPECIFIER ** Select from the following two (2) subparagraphs for the width of the passageway
1. 800 mm (31 1/2 in)
2. 900 mm (35 3/7 in)
AF. Dimensions for Left, Intermediate and Right Cabinets
1. Cabinet Length: 1200 mm (47 in) maximum
2. Cabinet Height: 1020 mm (40 1/6 in)
3. Cabinet Width: 450 mm (17 5/7 in) maximum
2.04 OPERATION
AG. Normal Operation (available for “Normally Closed & Controlled” configuration)
1. In stand-by position, the passageway shall be securely blocked by means of retractable doors

2. Upon receipt of opening pulse from the access control system the doors shall retract into the housing, consequently freeing the passageway
3. The doors immediately close after passage or after an adjustable time-out

4. If an unauthorised person follows an authorised person (tailgating) or attempts to enter from the opposite direction, the unit shall detect the unauthorised passage and activate the alarm conditions
AH. Emergency Operation

1. The unit shall have an input in order to receive the “fire alarm” signal. When the emergency signal is activated, the unit shall react in the following way:

a. Doors open and remain open

b. Green arrow signals are displayed on the pictograms in both directions

2. This operating mode continues as long as the emergency signal is active. After the emergency signal has been turned off, the unit shall return in its previous operating mode.
AI. Power Failure
1. In case of power failure, the security entrance lane shall be opened by intrinsic mechanical energy (Fail-Safe), without any back-up battery or equivalent
2. After the power supply has been restored, the unit shall return to its previous operating mode.

2.05 SECURITY
AJ. Shall provide retractable doors to securely block the passageway:

** NOTE TO SPECIFIER ** 1000 mm half-height doors are the standard height for the SmartLane 910 Security Entrance Lane. For an additional cost, other heights are available as options listed in brackets for enhanced physical security.
Delete the following subparagraphs in brackets if no optional height is required, or retain the height that is appropriate for the project.

1. 1000 mm (39 3/8 in) half-height doors
2. [1200 mm (47 in) half-height doors and anti-climb panels made of 12 mm thick clear tempered glass]
3. [1700 mm (67 in) full-height doors and anti-climb panels made of 12 mm thick clear tempered glass]
4. [1900 mm (74 in) full-height doors and anti-climb panels made of 12 mm thick clear tempered glass]
AK. Shall have a mechanical locking integrated. The doors shall be mechanically blocked by crank-and-rod linkage in closed position to prevent any attempted break-in
AL. Passage shall be electronically controlled in both directions to detect and deter unauthorised person entering into the secure area:
1. Passage with an unauthorised means of authentication
2. Passage in the opposite direction

3. Unauthorised person following an authorised person, i.e tailgating

4. Obstruction of an infrared beam path
AM. The security entrance lane shall ensure that one valid authentication allows only one valid entry to the restricted area by using infrared sensors to determine the direction of the passage and number of pedestrians passing through the passageway at one time
AN. Passage shall be electronically controlled in both directions by a minimum of ten (10) sensors
AO. In the event of detection of an unauthorised behaviour, the unit shall close the door and activates the alarm conditions.
2.06 SAFETY
AP. In case of emergency or power failure, the retractable doors shall be opened by intrinsic mechanical energy (Fail-Safe), without any back-up battery or equivalent

AQ. Sensors shall be deployed at a minimum of three (3) different heights to ensure user safety: there shall be sensors at approximately ankle height, knee height and waist height.
AR. The unit shall have user safety sensors to prevent doors from closing when a user is standing between the doors. 

For general public applications, additional safety sensors insuring enhanced user protection are recommended:

** NOTE TO SPECIFIER ** Safety sensors are integrated as a standard to ensure user protection. For an additional cost, additional safety sensors are available as options listed in brackets for enhanced protection.
Delete the following subparagraphs in brackets if no additional safety sensors are required, or retain the functionality(functionalities) that is (are) appropriate for the project.

1. [Additional safety sensors for enhanced user protection]
2. [Additional safety sensors for enhanced trolley protection in entrance direction]
3. [Additional safety sensors for enhanced trolley protection in exit direction]
4. [In the case of full-height doors (1200mm, 1700 mm or 1900 mm (47 in, 67 in or 74 in)), additional safety sensors implemented in the fixed plan leaves shall be available]
** NOTE TO SPECIFIER ** The safety shutter is available as a standard for unit equipped with retractable doors higher than 1000mm.

Retain the following subparagraph if the previously selected glass retractable doors are higher than 1000 mm.
AS. [In the case of full-height doors (1200mm, 1700 mm or 1900 mm (47 in, 67 in or 74 in)), the unit shall be equipped with safety shutter applied to the cabinet’s top apertures to prevent users from introducing body parts in the space left open during operation]
AT. Shall be equipped with inductive sensors to control the position of the mobile doors with high precision and be able to stop door’s movement when an obstacle is detected
** NOTE TO SPECIFIER ** The rubber edges for glass doors are an available option for doors higher than 1000mm. For an additional cost, glass doors equipped with rubber edges are available as options listed in brackets to enhance user protection and comply with limitations of door forces DIN 18650-1:2005-12 and prEN 12650-1:1996 standards.
Delete the following subparagraph in brackets if no compliance with limitations of door force standards isrequired, or retain as necessary (only if the previously selected glass doors are higher than 1000 mm).
AU. [In order to enhance users’ safety and protection, rubber edges can be applied to the doors. Equipped with such rubber bumpers, the security entrance lane shall comply with limitations of door forces in accordance with DIN 18650-1:2005-12 and prEN 12650-1:1996 standards]
2.07 PEDESTRIAN GUIDANCE
AV. Visual notification with clear graphics shall be incorporated into each passageway (one for each direction) to provide status of the lane, to control flow and to warn users

** NOTE TO SPECIFIER ** Orientation pictogram is the standard visual notification. For an additional cost, a function pictogram is available as an option listed in brackets for enhanced user guidance.
Delete the following subparagraph in brackets if no additional function pictogram is required, or retain as necessary.

AW. [To improve user guidance, the security entrance lane can integrate an additional visual notification for indication of valid or invalid authentication]
AX. Audible notification shall be incorporated into each passageway to provide status of the lane and alarm conditions with two (2) distinctive audible tones
1. First stage notifies user and guard that someone has entered the lane without authorisation
a. Allows user to attempt authorisation, before going into a full alarm
b. Guard is notified that a lane violation may occur
2. Second stage notifies user and guard that someone has passed through the lane without authorisation
a. Notifies the users that they have passed through the lane without authorisation
b. Guard is notified that a lane violation has occurred and takes appropriate actions
2.08 DRIVE UNIT
AY. Three-phase asynchronous geared motor combined with crank-and-rod linkage ensuring perfect mechanical locking in both extreme positions
AZ. Variable-speed controller ensuring progressive accelerations and gradual decelerations, for a safe movement without vibrations
BA. Inductive sensors to control the absolute position of the mobile leaves with high precision

2.09 CONTROLLER
BB. Microprocessor-based controller with the following characteristics:
1. RAM & ROM memory

2. CAN Bus interface

3. LCD display to set operating modes, advanced parameters and to provide diagnostics for quick detection of problem source
4. LED indicators showing the status of the inputs and outputs
5. RS232 communication interface for extended settings and functions
2.010 POWER SUPPLY
BC. Power supply:

** NOTE TO SPECIFIER ** 230 Volts AC 50/60 Hz is the standard power supply. For an additional cost, 120 Volts AC 60 Hz is available as an option in brackets.

Retain one of the two following subparagraphs that is appropriate for the project.

1. 230 Volts AC 50/60 Hz
2. [120 Volts AC 60 Hz]
BD. Nominal consumption in operation: 250 W maximum
2.011 PERFORMANCES
BE. Opening Time & Closing Time

1. The opening time of the doors shall be from 0.3 to 0.9 seconds

2. The closing time of the doors shall be from 0.5 to 1.0 seconds

BF. MCBF: 2.500.000 average number of cycles between breakdowns, when respecting recommended maintenance

BG. Operating Temperatures: 0 to +50 degrees Celsius (+32 to +122 degrees Fahrenheit)
2.012 OPTIONAL EQUIPMENT
** NOTE TO SPECIFIER ** Delete the following subparagraphs in brackets if no optional equipment is required, or add as necessary.
1. [Side panels with customised RAL xxxx paint (to be specified)]
2. [Customised glass doors with pattern or logo]
PART III – EXECUTION
2.013 INSPECTION
BH. Installer must examine the installation location and advise the Contractor of any site conditions inconsistent with proper installation of the product. These conditions include but are not limited to the following:
1. Security entrance lane must be installed on a level concrete pad
2. Power supply and control wiring must be installed. Follow manufacturer’s recommendations
BI. Proceed with installation only after unsatisfactory conditions have been corrected.

2.014 INSTALLATION
BJ. Install security entrance lane in strict accordance with manufacturer’s instructions. Set units level. Anchor securely into place.
2.015 ADJUSTMENT
BK. Installer shall adjust security entrance lane for proper performance after installation.

2.016 INSTRUCTION
BL. A factory trained installer shall demonstrate to the owner’s maintenance crew the proper operation and the necessary service requirements of the equipment, including exterior maintenance. 

2.017 CLEANING
BM. Clean turnstile and area carefully after installation to remove excess caulk, dirt and labels.

2.018 MAINTENANCE
BN. Maintain the equipment according to the manufacturer’s instructions.
Automatic Systems reserves the right to change this specification at any time without notice.
END OF SECTION

SmartLane910-ES-EN-00

                                                                                      SECTION 11 14 00 - 1
SmartLane910-ES-EN-00

                                                                                      SECTION 11 14 00 - 2

[image: image1.png]